## Sheet1
|  |  | Online Testing | [6 empty] | Offline Testing
Rev. 2.2 | Reference to Job Aids (Equipment Specific) | Table is indicating testing frequency in years. The test frequencies indicate Cargill minimum requirements. Local rules and regulations might request shorther test periods. In any case, the shortest period applies. 1,2,3,4,5 = Schedule in years M = Monthly Q = Quarterly X = Test before use A = Recommended additional fault finding measurement C = Comissioning or Re-comissioning after repair Safety relevant tests and tests required by the insurance comapny or legally required tests are marked in red | Visual Inspection (during operation) 30 | Oil Sample Analysis | Infrared Inspection | Ultrasonic Emission Surveys | Online Partial Discharge Testing | Battery Tests | Online MCA (Motor Circuit Analysis) | Physical Inspection (requires shutdown) | Dielectric Overpotential (HiPot) DC for LV or VLF for HV | Offline Partial Discharge (with surge or VLF) Testing | VLF tan delta test | Insulation Resistance | Contact/Connection Resistance | Fuse Resistance | Power Factor/ Dissipation Factor | Winding Resistance | Vacuum Bottle Integrity | Electrical Operability Test, Current injection, Adjustment, Calibration, Lubrication | Mechanical Operability Test (breaker exercise) | Capacitance Test | Ground/Earth Resistance | Grounding/Bonding Continuity Test | System Operability / Load Test | Loop impedance test | Shield continuity test | IEC Ex inspections | Offine MCA (Motor Circuit Analysis) | Comments
Reference to RE Work Execution Standard (Task Specific) |  |  | A0 | A2 | A3 | A4 | A5 | A6 | 23 | A1 | A7 | A24 | A25 | A8 | A9 | A10 | A11 | A12 | A13 | A14 | A15 | A16 | A17 | A18 | A19 | A20 | A21 | A22 | A26 | 30, 33, 34, 36, 37, 39
High Voltage (HV & MV), >1000V | Transformer
| J4 | Transformer, Oil-Filled >500 KVA (incl. OLTC) | A0: 1; A2: 1; A3: 1-3; A4: 1-3; A1: 3-5; A18: 3-5 | 1, 38
| J5 | Transformer, Oil-Filled >= 5000 KVA (incl. OLTC) | A0: 1; A2: 1; A3: 1-3; A4: 1-3; A1: 3-5; A8: 3-5; A11: 3-5; A12: 3-5; A18: 3-5 | 1, 38
| J6 | Transformer, Dry-Type >500 KVA | A0: 1; A3: 1-3; A4: 1-3; A1: 3-5; A18: 3-5
| J7 | Transformer, Dry-Type >= 5000 KVA | A0: 1; A3: 1-3; A4: 1-3; A1: 3-5; A8: 3-5; A12: 3-5; A18: 3-5
Switches
| J16 | Breakers(Short Circuit Breaker), HV Air | A0: 1; A3: 1-3; A4: 1-3; A8: 3-5; A9: 3-5; A14: 3-5; A15: 1-2 | 19
| J16 | Breakers(Short Circuit Breaker), HV Vacuum | A0: 1; A3: 1-3; A4: 1-3; A8: 3-5; A9: 3-5; A13: 3-5; A14: 3-5; A15: 1-2 | 19
| J16 | Breakers(Short Circuit Breaker), HV Oil | A0: 1; A2: 1; A3: 1-3; A4: 1-3; A8: 3-5; A9: 3-5; A14: 3-5; A15: 1-2 | 2, 19
| J16 | Breakers(Short Circuit Breaker), HV SF6 | A0: 1; A3: 1-3; A4: 1-3; A8: 3-5; A9: 3-5; A14: 3-5; A15: 1-2 | 19
| J17 | Switches, HV Air (with or without fuse) | A0: 1; A3: 1-3; A4: 1-3; A8: 3-5; A9: 3-5; A10: 3-5; A14: 3-5; A15: 3-5
| J17 | Switches, HV Vacuum (with or without fuse) | A0: 1; A3: 1-3; A4: 1-3; A8: 3-5; A9: 3-5; A10: 3-5; A13: 3-5; A14: 3-5; A15: 3-5
| J17 | Switches, HV SF6 (with or without fuse) | A0: 1; A3: 1-3; A4: 1-3; A8: 3-5; A9: 3-5; A10: 3-5; A14: 3-5; A15: 3-5
Switchgear/-board
| J18 | Switchgear/Switchboard (including MCC), HV Air | A0: 1; A3: 1-3; A4: 1-3; A5: 1; A1: 3-5; A8: 3-5; A9: 3-5; A18: 3-5
| J18 | Switchgear/Switchboard (including MCC), HV SF6 | A0: 1; A3: 1-3; A4: 1-3; A5: 1; A1: 3-5; A8: 3-5; A9: 3-5; A18: 3-5
| J45 | Main feeding Busbars Air Insulated HV, External | A0: 1; A3: 1-3; A4: 1-3; A5: 1; A1: 3-5; A7: A, C; A8: 3-5; A9: 3-5; A18: 3-5 | 4
| J41 | Protection Relays HV, LV | A0: 1; A1: 3-5; A14: 3-5 | 18
| - | Metering, HV, LV
| J43 | Surge/Lightning Arresters | A0: 1; A3: 1-3; A4: 1-3; A1: 3-5; A8: 3-5; A9: 3-5; A11: 3-5
| J44 | Power Factor Correction PFC (Capacitors incl. Reactors), HV | A0: 1; A3: 1-3; A4: 1-3; A1: 3-5; A8: 3-5; A16: 3-5; A19: 3-5
Cables
| J60 | Cable, HV | A0: 1; A4: 1-3; A5: 1; A1: 3-5; A7: A, C; A24: A, C; A25: 3-5; A8: 3-5; A9: 3-5; A21: 3-5 | 6, 25, 26
| J62 | Overhead power line, HV | A0: 1; A3: 1-3; A4: 1-3; A1: 5-10; A17: 3-5 | 35
Motor starters
| J46 | Starters (Contactors), HV Vacuum | A0: 1; A3: 1-3; A4: 1-3; A8: 3-5; A9: 3-5; A13: 3-5; A14: 3-5; A15: 1-2
| J46 | Starters (Contactors), HV Air | A0: 1; A3: 1-3; A4: 1-3; A8: 3-5; A9: 3-5; A14: 3-5; A15: 1-2
| J47 | Variable Speed Drive VSD, HV | A0: 1; A3: 1-3; A4: 1-3; A18: 1
| J48 | Softstarter, HV | A0: 1; A3: 1-3; A4: 1-3; A18: 1
Rotating machines
| J50 | Motor, HV | A0: 1; A5: 1; 23: A; A8: 1; A12: 1; A18: 1; A22: 2-3; A26: A | 24
| J51 | Generator, HV | A0: 1; A3: 1-3; A5: 1; A8: 1; A12: 1; A18: 1 | 24
Low Voltage (LV), <1000V | Switches
| J8 | Breakers, LV Power >400A (inlcuding trip units) | A0: 1; A3: 1-3; A8: 3-5; A9: 3-5; A10: 3-5; A14: 3-5; A15: 1-2 | 19, 20
| J9 | Breakers, LV Molded Case >400A (inlcuding trip units) | A0: 1; A3: 1-3; A8: 3-5; A9: 3-5; A14: 3-5; A15: 1-2 | 19
| J10 | Breakers, LV Insulated Case >400A (inlcuding trip units) | A0: 1; A3: 1-3; A8: 3-5; A9: 3-5; A14: 3-5; A15: 1-2 | 19, 20
| J11 | Switches, LV (>400A) | A0: 1; A3: 1-3; A8: 3-5; A9: 3-5; A10: 3-5; A14: 3-5; A15: 3-5
Switchgear/-board
| J19 | Switchgear/Switchboard (including MCC), LV | A0: 1; A3: 1-3; A1: 3-5; A8: 3-5; A9: 3-5; A18: 3-5
| J40 | Main feeding busbars, LV, External | A0: 1; A3: 1-3; A8: 3-5; A9: 3-5; A18: 3-5 | 4
| J42 | Power Factor Correction PFC (Capacitors incl. Reactors), LV | A0: 1; A3: 1-3; A1: 3-5; A8: 3-5; A16: 1-2; A19: 1-2
Motor starters
| J20 | Starters (Contactors), fixed mounted, LV | A0: 1; A3: 1-3; A14: 3-5
| J21 | Starters (Contactors), withdrawable, LV | A0: 1; A3: 1-3; A1: 1; A14: 3-5
| J24 | Variable Speed Drives VSD, LV | A0: 1; A3: 1-3; A18: 1 | 22
| J25 | Softstarters, LV | A0: 1; A3: 1-3; A18: 1 | 22
Cables
| J61 | Cables, LV | A0: 1; A7: A, C; A8: 3-5; A9: 3-5 | 26
| J62 | Overhead power line, LV | A0: 1; A3: 1-3; A1: 5-10; A17: 3-5 | 35
Back-up Power
| J14 | UPS System | A0: 1; A3: 1-3; A19: 1
| J15 | Batteries, Sealed and Vented | A0: 1; A3: 1-3; A6: 1; A9: 1; A19: 2 | 5, 7, 8
| J12 | DC power supply | A0: 1; A3: 1-3; A19: 1
| J13 | Battery Charger | A0: 1; A3: 1-3; A19: 1
Grounding / Earthing System
| J31 | Grounding and Bonding for structures and electr. Systems | A0: 1; A1: 1; A17: 3-5; A18: 3-5 | 17
| J29, J31 | Lightning protection | bar: A0 to A26
| J30 | Ground Fault Indication (HRG/LRG/IT) | A0: 1; A14: 3-5
Field Installation
| J22 | Socket-outlets | A0: 1; A18: 5; A20: 5; A22: 2-3 | 9, 10
| J34 | Junction boxes | A0: 1; A18: 3-5; A22: 2-3
| J1 | RCDs /GFCIs | A0: 1; A14: 5; A15: 0.5 | 11
| J35 | Disconnect / Field Work Switches | A0: 1; A1: 1; A8: 3-5; A9: 3-5; A14: 3-5; A18: 3-5; A22: 2-3 | 21,27
| - | Start/Stop Stations / Local Control Switches | A0: 1; A22: 2-3
| - | Emergency Stop circuits | A0: 1; A19: TBD | 41
| J32 | Conduit and cable tray systems (race ways) | A0: 1; A18: 3-5; A22: 2-3 | 12
| J36 | Cathodic protection for undergorund tanks | A0: 1; A19: 1-2
Heating
| J70 | Electrical Heaters | bar: A0 to A26
| J71 | Heat tracing | A0: 1; A8: 1-2; A19: 1-2; A22: 2-3 | 28, 29
Portable/Temporary Devices
| J3 | Portabel RCD / GFCIs | bar: A0 to A26
| J2 | Portable Tools / Equipment incl. Extension Cords (field) | A0: X; A1: Q; A8: Q; A18: Q; A22: 0.5 - 1 | 3, 13,14, 40
| J2 | Portable Tools / Equipment incl. Extension Cords (office) | [27 empty] | 3, 31 | bar: A0 to A26
Electrical Rooms
| J23 | Electrical Room | bar: A0 to A26
Lighting
| J37 | Lighting fixtures (including switches) | A0: 1; A22: 2-3
| J33 | Emergency Lighting | A0: 1; A19: M , 1; A22: 2-3 | 15, 16
Fire Detection System
| - | Detectors | bar: A0 to A26
| - | Monitoring / Control System | bar: A0 to A26
Rotating machines
| J52 | Motor, LV | A0: 1; 23: A; A8: 1; A12: 1; A18: 1; A22: 2-3; A26: A | 21, 32
| J53 | Generator, LV | A0: 1; A3: 1-3; A8: 1; A12: 1; A18: 1; A19: 1
Instrumentation
| - | Field instruments | A22: 2-3
| - | Proecess Instrumentation, Generic | A22: 2-3
Related Job aids and Work Execution standards are guidelines only and not part of the policy and procdure
Comments
| 1 | For hermetically sealed oil-filled transformers without N2 blanket an oil sample analysis is not requested unless deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets)
| 2 | Sealed Minimum Oil Breakers are not included.
| 3 | Test is not required for double insulated devices
| 4 | External/outside buses and open switchgear/switchboards
| 5 | Recommendation for schedule is derived from NETA and IEEE: 25% of life expectancy or 2 years - whatever is less
| 6 | Only required if deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets); usually not done for single motor cables
| 7 | Tests are not required if the battery system is continuously monitored with a battery management system, providing similar functionality as described in the Job Aid J15
| 8 | Tests are required only for battery systems that supply plant critical loads (eg for HV protection relays, emergency systems or UPS systems)
| 9 | Only required for sockets which are not protected by GFCI/RCD
| 10 | Only required if no calculation document or specific MOC-procedure is in place
| 11 | 25% of the installed devices (randomly selected) within each plant area shall be tested. A 100% follow-up testing is required if the failure rate exceeds 2%.
| 12 | A sampling tests is sufficient. Select test points in all plant areas.
| 13 | Test is only required if it cannot be ensured that the portable tool is always used with a portable GFCI/RCD
| 14 | It is required that all portable tools and extension cords in the field are used with portable GFCI/RCD. In cases where - due to whatever reason - an upstream GFCI/RCD is not used, only tools and devices shall be used which are regularly tested (quarterly) as indicated by the EMP.
| 15 | Monthly test to verify lights go on and a yearly capacity test for all lamps for the time as specified by local code.
| 16 | Monthly functional tests are not required for emergency lighting systems that are monitored continously - a visual check of the indicaiton is sufficient
| 17 | Frequency for classified (ATEX Class 1/2 Div 1/2) areas is reduced to once per year
| 18 | Mandatory for overcurrent protection functions (ANSI/IEEE 50/51) and for earth fault protection functions (ANSI/IEEE 50N/51N); Recommended for all other protection functions
| 19 | Circuit breakers should be fully inspected after a severe high energy shutdowns (eg if trip was caused by short time or instantaneous or magnetic trip or if there is proof of a short circuit or arc downstream which was cleared by the breaker)
| 20 | Only applicable if fitted (usually ACB, PCB and ICCB do not have fuses inside, but some will have it, especially in NA)
| 21 | Due to the amount of LV motors installed and operated at Cargill facilities it is recommended to limit the scope to the following LV motors: Only black and grey assets which are • Difficult to replace (eg big motors, motor in difficult locations, etc.) OR • Expensive (eg big motors, classified areas, special motors etc.) OR • No spare parts available OR • Do cause a significant downtime or production cost which exceeds the maintenance costs over the lifetime of the motor The selection of the motors subject to receive maintenance is made by the local RE team
| 22 | An additiional preventive replacement program is suggested on top of the inspections in the matrix - refer to job aid for further information
| 23 | Not used
| 24 | PD measurement for 6kV and above only as part of the surge testing
| 25 | PD recommended as additional fault finding tool if tan delta or insualtion resistances measurement indicates issues; Offline PD in combination with VLF is preferred.
| 26 | This test is focussing on the cable conneciton and not on the complete run of the cable. It is recommended to do this test in combination with the test of the equipment/switchgear.
| 27 | Tests A08, A09 and A14 only need to be executed if they are not already executed together with the testing of the motor (motors can be tested from the MCC drawer/bucket, which will also test the components in between)
| 28 | Test A08 shall only be required if the heat trace circuit is not protected with a GFCI/GFEP/RCD
| 29 | It is recommended to test HT systems yearly before the start of the cold season to ensure they are operational
| 30 | The individual job aids do not distinguish between Safety and RE specific inspeciton points. While only the safety relevant points are required to be checked during the visual inspection it is recommended to include all RE ones as the addional required to execute the task is usually estimated to be minimal
| 31 | Test is not required, if the facility has all socket outlets protected with fixed mounted RCD/GFCI
| 32 | Online MCA not a mandatory test - see position paper E-PP-003 Online MCA for further guidance. It is only allowed to execute Online MCA if it can be done safely, as described in the position paper E-PP-003.
| 33 | For A22: Lot size for sampling inspection can be based on the electical proteciton type - see WE standard A22 for details; see further comments in note 34
| 34 | For A22: This inspection is required by IEC code for countries regulated by IEC and by ATEX for the European Union: • Equipment has be to inspected periodically wth Visual and Close inspecitons every three years; Close inspection is only reuqired for non-IC equipment; periodic inspeciton can be omitted, if a plant follows the requirements for continuous supervision • Sample inspection with Detailed Inspeciton grade is required in between peridic inspections
| 35 | Adjust the schedule on the overall conditions and the ambient conditions. A suspicion or finding during the visual inspection A0 can warrant an immedeate physical inspeciton out of the normal scheduled inspection.
| 36 | Test are mandated for the following equipment - for all other equipment, the test is recommended: 1. For facilities which are insured by the Minnetonka insurance company and which are either hatcheries, plants with production coolers/freezers, or operate 24/7, all electrical equipment according to the RE WE standard need to be inspected every year 2. For all other facilities which are insured by the Minnetonka insurance company all electrical equipment according to the RE WE standard need to be inspected every three years (examples are facilities that operate seasonally)
| 37 | Test are mandated for the following equipment - for all other equipment, the test is recommended: 1. For facilities which are insured by the Minnetonka insurance company and which are either hatcheries, plants with production coolers/freezers, or operate 24/7, all HV electrical equipment according to the RE WE standard need to be inspected every year 2. For all other facilities which are insured by the Minnetonka insurance company all HV electrical equipment according to the RE WE standard need to be inspected every three years (examples are facilities that operate seasonally)
| 38 | Test are mandated by Minnetonka Insurance Company for the following equipment - for all other equipment, the test is recommended: 1. For all transformers >= 500 kVA with Mineral Oil filling, if they are installed inside buildings or on roof tops the test is classified as mandatory - for other transformers it is recommended 2. For all transformers >5000 kVA independent of the insulation medium
| 39 | Informational note: Depending on selected test method and installation methods this test can be done online or offline
| 40 | According to IEC 60079-19, testing must be done yearly. Enclosures which are opened freuqntly (such as batteriy housings) must be inspected every 6 month
| 41 | Functionality of EM stop cirucits must be verified. It is currently unlcear if this should be incorporated in the EMP or if this should be part of an overall machinery safety program, that would include the testing of Safety Instzrumentaiton Loops (aka CSD) as part of the SIS
Note on D2: Comment 30: The individual job aids do not distinguish between Safety and RE specific inspeciton points. While only the safety relevant points are required to be checked during the visual inspection it is recommended to include all RE ones as the addional required to execute the task is usually estimated to be minimal
Note on H2: Andreas Lehr: Online PD is accpeted to replace offline PD for cables. Measurement is then done at power frequency
Note on M2: Andreas Lehr: Offline PD in combination with surge testing is recommended for motors/generators Offline PD in combinaiton with VLF is recommended as additional fault finding on cables.
Note on R2: Andreas Lehr: Need to check which standards have been referenced for voltage and duration - IEC or IEEE - see also word document in folder for A7
Note on AD2: Andreas Lehr: Do we want to write a WE standard for online MCA as well: It is currently mentiuoend in the job aids
Note on F3: Comment 36: Test are mandated by Minnetonka Insurance Company for the following equipment - for all other equipment, the test is recommended: 1. For facilities which are insured by the Minnetonka insurance company and which are either hatcheries, plants with production coolers/freezers, or operate 24/7, all electrical equipment according to the RE WE standard need to be inspected every year 2. For all other facilities which are insured by the Minnetonka insurance company all electrical equipment according to the RE WE standard need to be inspected every three years (examples are facilities that operate seasonally)
Note on G3: Comment 37 Test are mandated by Minnetonka Insurance Company for the following equipment - for all other equipment, the test is recommended: 1. For facilities which are insured by the Minnetonka insurance company and which are either hatcheries, plants with production coolers/freezers, or operate 24/7, all HV electrical equipment according to the RE WE standard need to be inspected every year 2. For all other facilities which are insured by the Minnetonka insurance company all HV electrical equipment according to the RE WE standard need to be inspected every three years (examples are facilities that operate seasonally)
Note on W3: Comment 39: Informational note: Depending on selected test method and installation methods this test can be done online or offline
Note on X3: Comment 39: Informational note: Depending on selected test method and installation methods this test can be done online or offline
Note on Y3: Comment 39: Informational note: Depending on selected test method and installation methods this test can be done online or offline
Note on AA3: Comment 39: Informational note: Depending on selected test method and installation methods this test can be done online or offline
Note on AC3: Comment 33: Lot size for sampling inspection can be based on the electical proteciton type - see WE standard A22 for details; see further comments in note 34 Comment 34: This inspection is required by IEC code for countries regulated by IEC and by ATEX for the European Union: • Equipment has be to inspected periodically wth Visual and Close inspecitons every three years; Close inspection is only reuqired for non-IC equipment; periodic inspeciton can be omitted, if a plant follows the requirements for continuous supervision • Sample inspection with Detailed Inspeciton grade is required in between peridic inspections
Note on E5: Comment 1: For hermetically sealed oil-filled transformers without N2 blanket an oil sample analysis is not requested unless deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets) Comment 38: Test are mandated by Minnetonka Insurance Company for the following equipment - for all other equipment, the test is recommended: 1. For all transformers >= 500 kVA with Mineral Oil filling, if they are installed inside buildings or on roof tops the test is classified as mandatory - for other transformers it is recommended 2. For all transformers >5000 kVA independent of the insulation medium
Note on E6: Comment 1: For hermetically sealed oil-filled transformers without N2 blanket an oil sample analysis is not requested unless deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets) Comment 38: Test are mandated by Minnetonka Insurance Company for the following equipment - for all other equipment, the test is recommended: 1. For all transformers >= 500 kVA with Mineral Oil filling, if they are installed inside buildings or on roof tops the test is classified as mandatory - for other transformers it is recommended 2. For all transformers >5000 kVA independent of the insulation medium
Note on U10: Comment 19: Circuit breakers should be fully inspected after a severe high energy shutdowns (eg if trip was caused by short time or instantaneous or magnetic trip or if there is proof of a short circuit or arc downstream which was cleared by the breaker)
Note on U11: Comment 19: Circuit breakers should be fully inspected after a severe high energy shutdowns (eg if trip was caused by short time or instantaneous or magnetic trip or if there is proof of a short circuit or arc downstream which was cleared by the breaker)
Note on E12: Comment 2 This test applies only for Bulk Oil Circuit Breakers, but not for Minimum Oil Circuit Breakers (see Job Aid J16 for details)
Note on U12: Comment 19: Circuit breakers should be fully inspected after a severe high energy shutdowns (eg if trip was caused by short time or instantaneous or magnetic trip or if there is proof of a short circuit or arc downstream which was cleared by the breaker)
Note on U13: Comment 19: Circuit breakers should be fully inspected after a severe high energy shutdowns (eg if trip was caused by short time or instantaneous or magnetic trip or if there is proof of a short circuit or arc downstream which was cleared by the breaker)
Note on C19: Andreas Lehr: We give currently no credit to the SF6 panel for reduced maintenance; Write separate job aid? Call differences out in the matrix? - Omit some tasks (e.g. contact resistance) - Longer test schedules (e.g. insulaiton resistance)?
Note on C20: Comment 4: External/outside buses and open switchgear/switchboards
Note on K21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Suggest to change this from 1 to 3-5; we might need to go back to J41, because the phyiscal test described for digital requires does not really require a shutdown.
Note on U21: Comment 18: Mandatory for overcurrent protection functions (ANSI/IEEE 50/51) and for earth fault protection functions (ANSI/IEEE 50N/51N); Recommended for all other protection functions
Note on C26: Andreas Lehr: OK to include all cables less than 10kV, e.g. important motor cables, feeding cbales form 6kV or 4160V to HV MCC, etc. 10kV statement removed October 2018
Note on F26: Comment 26: This test is focussing on the cable conneciton and not on the compelte run of the cable. It is recommended to do this test in combination with the test of the equipment/switchgear.
Note on G26: Comment 26: This test is focussing on the cable conneciton and not on the compelte run of the cable. It is recommended to do this test in combination with the test of the equipment/switchgear.
Note on H26: Comment 26: This test is focussing on the cable conneciton and not on the compelte run of the cable. It is recommended to do this test in combination with the test of the equipment/switchgear.
Note on I26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For on-line partial discharge testing, why does the comment say it doesn't test the entire length of the cable. Depending on the type of connection it does test the entire length.
Note on K26: Comments 6 Only required if deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets)
Note on M26: Comment 25: PD recommended as additional fault finding tool if tan delta or insualtion resistances measurement indicates issues; Offline PD in combination with VLF is preferred.
Note on N26: Comments 6 Only required if deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets)
Note on O26: Comments 6 Only required if deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets)
Note on P26: Comments 6 Only required if deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets)
Note on AB26: Comments 6 Only required if deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets)
Note on F27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Job aid 62 calls for IR and UE inspections. Seems valid for at least uninsulated lines. For insulated lines, should we do insulation resistance test and other testes recommended for cable HV? similar comments (except UE) for LV OH lines.
Note on K27: Note 35: Adjust the schedule on the overall conditions and the ambient conditions. A suspicion or finding during the visual inspection A0 can warrant an immedeate physical inspeciton out of the normal scheduled inspection.
Note on F34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: It is currently included in J50, but it is not done on LV motors. why would be do it on HV motors, but not on large LV motors? I suggest to delete it.
Note on H34: Comment 24: PD measurement for 6kV and above only as part of the surge testing
Note on H35: Comment 24: PD measurement for 6kV and above only as part of the surge testing
Note on Q37: Comment 20: Only applicable if fitted (usually ACB, PCB and ICCB do not have fuses inside, but some will have it, especially in NA)
Note on U37: Comment 19: Circuit breakers should be fully inspected after a severe high energy shutdowns (eg if trip was caused by short time or instantaneous or magnetic trip or if there is proof of a short circuit or arc downstream which was cleared by the breaker)
Note on U38: Comment 19: Circuit breakers should be fully inspected after a severe high energy shutdowns (eg if trip was caused by short time or instantaneous or magnetic trip or if there is proof of a short circuit or arc downstream which was cleared by the breaker)
Note on Q39: Comment 20: Only applicable if fitted (usually ACB, PCB and ICCB do not have fuses inside, but some will have it, especially in NA)
Note on U39: Comment 19: Circuit breakers should be fully inspected after a severe high energy shutdowns (eg if trip was caused by short time or instantaneous or magnetic trip or if there is proof of a short circuit or arc downstream which was cleared by the breaker)
Note on C43: Comment 4: External/outside buses and open switchgear/switchboards
Note on U46: Comment 5: Only required if deemed critical defined by maintenance and reliability definitions.
Note on U47: Comment 5 Only required if deemed critical defined by maintenance and reliability definitions.
Note on C48: Comment 22: An additiional preventive replacement program is suggested on top of the inspections in the matrix - refer to job aid for further information
Note on C49: Comment 22: An additiional preventive replacement program is suggested on top of the inspections in the matrix - refer to job aid for further information
Note on F51: Comment 26: IR for cable connections is included in the equipment connected to the cable and this not listed for the cable iself. IR of cables on raceways is not foreseen.
Note on K52: Note 35: Adjust the schedule on the overall conditions and the ambient conditions. A suspicion or finding during the visual inspection A0 can warrant an immedeate physical inspeciton out of the normal scheduled inspection.
Note on I55: Comment 7: Tests are not required if the battery system is continuously monitored with a battery management system, providing similar functionality as described in the Job Aid J15 Comment 8: Tests are required only for battery systems that supply plant critical loads (eg for HV protection relays, emergency systems or UPS systems)
Note on Z55: Comment 5: Recommendation for schedule is derived from NETA and IEEE: 25% of life expectancy or 2 years - whatever is less Comment 8: Tests are required only for battery systems that supply plant critical loads (eg for HV protection relays, emergency systems or UPS systems)
Note on Y59: Comment 17: Frequency for classified (ATEX, Class 1/2 Div 1/2) areas is reduced to once per year
Note on Y63: Comment 9: Only required for sockets which are not protected by GFCI/RCD!
Note on AA63: Comment 10: Only required if no calculation document or specific MOC-procedure is in place.
Note on U65: Comment 11: 25% of the installed devices (randomly selected) within each plant area shall be tested. A 100% follow-up testing is required if the failure rate exceeds 2%.
Note on C68: Andreas Lehr: Emergency Stop (proteciton against mechancial movement) Emergency Switching off (protection against electrical shock) Red button on yellow ground
Note on Y69: Comment 12: A sampling tests is sufficient. Select test points in all plant areas.
Note on O73: Comment 28: Test A08 shall only be required if the heat trace circuit is not protected with a GFCI/GFEP/RCD
Note on Z73: Comment 29: It is recommended to execute this test before the winter periode to ensure the system is operable
Note on O75: Andreas Lehr: Removed all electrical tests (A08, A14, A18) because it is not an OEM requirement. From a risk profile the damage of the short pigtail which usually is hanging on the socket is reduced compared to the long extension cords that are laying on the ground.
Note on U75: Andreas Lehr: Removed all electrical tests (A08, A14, A18) because it is not an OEM requirement. From a risk profile the damage of the short pigtail which usually is hanging on the socket is reduced compared to the long extension cords that are laying on the ground.
Note on Y75: Andreas Lehr: Removed all electrical tests (A08, A14, A18) because it is not an OEM requirement. From a risk profile the damage of the short pigtail which usually is hanging on the socket is reduced compared to the long extension cords that are laying on the ground.
Note on C76: Comment 14: It is required that all portable tools and extension cords in the field are used with portable GFCI/RCD. In cases where - due to whatever reason - an upstream GFCI/RCD is not used, only tools and devices shall be used which are regularly tested (quarterly) as indicated by the EMP.
Note on K76: Comment 13: Test is only required if it cannot be ensured that the portable tool is always used with a portable GFCI/RCD
Note on O76: Comment 13: Test is only required if it cannot be ensured that the portable tool is always used with a portable GFCI/RCD
Note on Y76: Comment 3: Test is not required for double insulated devices Comment 13: Test is only required if it cannot be ensured that the portable tool is always used with a portable GFCI/RCD
Note on AC76: comment 40: According to IEC 60079-19, testing must be done yearly. Enclosures which are opened freuqntly (such as batteriy housings) must be inspected every 6 month
Note on O77: Comment 31: Test is not required, if the facility has all socket outlets protected with fixed mounted RCD/GFCI
Note on Y77: Comment 3: Test is not required for double insulated devices Comment 31: Test is not required, if the facility has all socket outlets protected with fixed mounted RCD/GFCI
Note on Z82: Comment 15: Monthly test to verify lights go on and a yearly capacity test for all lamps for the time as specified by local code. Comment 16: Monthly functional tests are not required for emergency lighting systems that are monitored continously - a visual check of the indicaiton is sufficient
Note on C87: Comment 21: Due to the amount of LV motors installed and operated at Cargill facilities it is recommended to limit the scope to the following LV motors: Only black and grey assets which are • Difficult to replace (eg big motors, motor in difficult locations, etc.) OR • Expensive (eg big motors, classified areas, special motors etc.) OR • No spare parts available OR • Do cause a significant downtime or production cost which exceeds the maintenance costs over the lifetime of the motor The selection of the motors subject to receive maintenance is made by the local RE team.
Note on P87: Andreas Lehr: Discussion with CCC EMEA - they see need to check terminations. This is in line with NETA MTS 2015, but would require to open the temrinal box - and for US to remove the electric tape …... Do we want to add contact resistance or re-torquing as part of A1? COE Meeting 03.10.2019 - risk of introducing a new failure mode is bigger than the benefit we expect to get. LEave it out
Note on Z88: Andreas Lehr: according to NFPA 110 Should be for critical loads RE
Note on C91: Comment Insteumentation is not part of EMP - in absence of a corporate instreumentaiton inspection matrix we decided to add this line to remind plants, that IECex inspecitons need to be done on instrumentiaon as well.
v
v
v
v
v
v
v
v
v
v
v
v

## Old Rev 2.1
Rev. 2.1 | Reference to Job Aids (Equipment Specific) | Table is indicating testing frequency in years. The test frequencies indicate Cargill minimum requirements. Local rules and regulations might request shorther test periods. In any case, the shortest period applies. 1,2,3,4,5 = Schedule in years M = Monthly Q = Quarterly X = Test before use A = Recommended additional fault location measurement C = Comissioning or Re-comissioning after repair Safety relevant tests are marked in red | Visual Inspection (during operation) 30 | Physical Inspection (requires shutdown) | Oil Sample Analysis | Infrared Inspection | Ultrasonic Emission Surveys | Partial Discharge ( with surge or VLF) Testing | Battery Tests | Dielectric Overpotential (HiPot) DC for LV or VLF for HV | Insulation Resistance | Contact/Connection Resistance | Fuse Resistance | PowerFactor/Dissipation Factor (VLF tan delta test) | Winding Resistance | Vacuum Bottle Integrity | Electrical Operability Test, Current injection, Adjustment, Calibration, Lubrication | Mechanical Operability Test (breaker exercise) | Capacitance Test | Ground/Earth Resistance | Grounding/Bonding Continuity Test | System Operability / Load Test | Loop impedance test | Shield continuity test | IEC Ex inspections | Online MCA (Motor Circuit Analysis) | Comments
Reference to RE Work Execution Standard (Task Specific) |  |  | A0 | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | A9 | A10 | A11 | A12 | A13 | A14 | A15 | A16 | A17 | A18 | A19 | A20 | A21 | A22 | A23
High Voltage (HV & MV), >1000V | Transformer
| J4 | Transformer, Oil-Filled >500 KVA (incl. OLTC) | A0: 1; A1: 3-5; A2: 1; A3: 1; A4: 1; A18: 3-5 | 1
| J5 | Transformer, Oil-Filled >= 5000 KVA (incl. OLTC) | A0: 1; A1: 3-5; A2: 1; A3: 1; A4: 1; A8: 3-5; A11: 3-5; A12: 3-5; A18: 3-5 | 1
| J6 | Transformer, Dry-Type >500 KVA | A0: 1; A1: 3-5; A3: 1; A4: 1; A18: 3-5
| J7 | Transformer, Dry-Type >= 5000 KVA | A0: 1; A1: 3-5; A3: 1; A4: 1; A8: 3-5; A12: 3-5; A18: 3-5
Switches
| J16 | Breakers(Short Circuit Breaker), HV Air | A0: 1; A3: 1; A4: 1; A8: 3-5; A9: 3-5; A14: 3-5; A15: 1-2 | 19
| J16 | Breakers(Short Circuit Breaker), HV Vacuum | A0: 1; A3: 1; A4: 1; A8: 3-5; A9: 3-5; A13: 3-5; A14: 3-5; A15: 1-2 | 19
| J16 | Breakers(Short Circuit Breaker), HV Oil | A0: 1; A2: 1; A3: 1; A4: 1; A8: 3-5; A9: 3-5; A14: 3-5; A15: 1-2 | 2, 19
| J16 | Breakers(Short Circuit Breaker), HV SF6 | A0: 1; A3: 1; A4: 1; A8: 3-5; A9: 3-5; A14: 3-5; A15: 1-2 | 19
| J17 | Switches, HV Air (with or without fuse) | A0: 1; A3: 1; A4: 1; A8: 3-5; A9: 3-5; A10: 3-5; A14: 3-5; A15: 3-5
| J17 | Switches, HV Vacuum (with or without fuse) | A0: 1; A3: 1; A4: 1; A8: 3-5; A9: 3-5; A10: 3-5; A13: 3-5; A14: 3-5; A15: 3-5
| J17 | Switches, HV SF6 (with or without fuse) | A0: 1; A3: 1; A4: 1; A8: 3-5; A9: 3-5; A10: 3-5; A14: 3-5; A15: 3-5
Switchgear/-board
| J18 | Switchgear/Switchboard (including MCC), HV Air | A0: 1; A1: 3-5; A3: 1; A4: 1; A8: 3-5; A9: 3-5; A18: 3-5
| J18 | Switchgear/Switchboard (including MCC), HV SF6 | A0: 1; A1: 3-5; A3: 1; A4: 1; A8: 3-5; A9: 3-5; A18: 3-5
| J45 | Main feeding Busbars Air Insulated HV, External | A0: 1; A1: 3-5; A3: 1; A4: 1; A7: A, C; A8: 3-5; A9: 3-5; A18: 3-5 | 4
| J41 | Protection Relays HV, LV | A0: 1; A1: 1; A14: 3-5 | 18
| - | Metering, HV, LV
| J43 | Surge/Lightning Arresters | A0: 1; A1: 3-5; A3: 1; A4: 3-5; A8: 3-5; A9: 3-5; A11: 3-5
| J44 | Power Factor Correction PFC (Capacitors incl. Reactors), HV | A0: 1; A1: 3-5; A3: 1; A4: 1; A8: 3-5; A16: 3-5; A19: 3-5
Cables
| J60 | Cable, HV | A0: 1; A1: 3-5; A5: A; A7: A, C; A8: 3-5; A9: 3-5; A11: 3-5; A21: 3-5 | 6, 25, 26
| J62 | Overhead power line, HV | A0: 1; A1: 5-10; A17: 3-5 | 35
Motor starters
| J46 | Starters (Contactors), HV Vacuum | A0: 1; A3: 1; A4: 1; A8: 3-5; A9: 3-5; A13: 3-5; A14: 3-5; A15: 1-2
| J46 | Starters (Contactors), HV Air | A0: 1; A3: 1; A4: 1; A8: 3-5; A9: 3-5; A14: 3-5; A15: 1-2
| J47 | Variable Speed Drive VSD, HV | bar: A0; A3 to A4; A18
| J48 | Softstarter, HV | bar: A0; A3; A18
Rotating machines
| J50 | Motor, HV | A0: 1; A3: 1; A5: 1; A8: 1; A12: 1; A18: 1; A22: 3; A23: A | 24
| J51 | Generator, HV | [24 empty] | 24 | bar: A0; A3; A5; A8; A12; A18
Low Voltage (LV), <1000V | Switches
| J8 | Breakers, LV Power >400A (inlcuding trip units) | A0: 1; A3: 1; A8: 3-5; A9: 3-5; A10: 3-5; A14: 3-5; A15: 1-2 | 19, 20
| J9 | Breakers, LV Molded Case >400A (inlcuding trip units) | A0: 1; A3: 1; A8: 3-5; A9: 3-5; A14: 3-5; A15: 1-2 | 19
| J10 | Breakers, LV Insulated Case >400A (inlcuding trip units) | A0: 1; A3: 1; A8: 3-5; A9: 3-5; A14: 3-5; A15: 1-2 | 19, 20
| J11 | Switches, LV (>400A) | A0: 1; A3: 1; A8: 3-5; A9: 3-5; A10: 3-5; A14: 3-5; A15: 3-5
Switchgear/-board
| J19 | Switchgear/Switchboard (including MCC), LV | A0: 1; A1: 3-5; A3: 1; A8: 3-5; A9: 3-5; A18: 3-5
| J40 | Main feeding busbars, LV, External | A0: 1; A3: 1; A8: 3-5; A9: 3-5; A18: 3-5 | 4
| J42 | Power Factor Correction PFC (Capacitors incl. Reactors), LV | A0: 1; A1: 3-5; A3: 1; A8: 3-5; A16: 1-2; A19: 1-2
Motor starters
| J20 | Starters (Contactors), fixed mounted, LV | A0: 1; A3: 1; A14: 3-5
| J21 | Starters (Contactors), withdrawable, LV | A0: 1; A1: 1; A3: 1; A14: 3-5
| J24 | Variable Speed Drives VSD, LV | [24 empty] | 22 | bar: A0 to A23
| J25 | Softstarters, LV | [24 empty] | 22 | bar: A0 to A23
Cables
| J61 | Cables, LV | A0: 1; A7: A, C; A8: 3-5; A9: 3-5 | 26
| J62 | Overhead power line, LV | A0: 1; A1: 5-10; A17: 3-5 | 35
Back-up Power
| J14 | UPS System | bar: A0 to A23
| J15 | Batteries, Sealed and Vented | A0: 1; A3: 1; A6: 1; A9: 1; A19: 2 | 5, 7, 8
| J12 | DC power supply | bar: A0 to A23
| J13 | Battery Charger | bar: A0 to A23
Grounding / Earthing System
| J31 | Grounding and Bonding for structures and electr. Systems | A0: 1; A1: 1; A17: 3-5; A18: 3-5 | 17
| J29 | Lightning protection | bar: A0 to A23
| J30 | Ground Fault Indication (HRG/LRG/IT) | A0: 1; A14: 3-5
Field Installation
| J22 | Socket-outlets | A0: 1; A18: 5; A20: 5; A22: 3 | 9, 10
| J34 | Junction boxes | A0: 1; A18: 3-5; A22: 3 | 33
| J1 | RCDs /GFCIs | A0: 1; A14: 5; A15: 0.5 | 11
| J35 | Disconnect / Field Work Switches | A0: 1; A1: 1; A8: 3-5; A9: 3-5; A14: 3-5; A18: 3-5; A22: 3 | 21,27
| J32 | Conduit and cable tray systems (race ways) | A0: 1; A18: 3-5; A22: 3 | 12, 33
| J36 | Cathodic protection for undergorund tanks | A0: 1; A19: 1-2
Heating
| J70 | Electrical Heaters | bar: A0 to A23
| J71 | Heat tracing | A0: 1; A8: 1-2; A19: 1-2; A22: 3 | 28, 29
Portable/Temporary Devices
| J3 | Portabel RCD / GFCIs | bar: A0 to A23
| J2 | Portable Tools / Equipment incl. Extension Cords (field) | [24 empty] | 3, 13,14 | bar: A0 to A23
| J2 | Portable Tools / Equipment incl. Extension Cords (office) | [24 empty] | 3, 31 | bar: A0 to A23
Electrical Rooms
| J23 | Electrical Room | bar: A0 to A23
Lighting
| J37 | Lighting fixtures (including switches) | A0: 1; A22: 3 | 33
| J33 | Emergency Lighting | A0: 1; A19: M , 1; A22: 3 | 15, 16, 33
Fire Detection System
| - | Detectors | bar: A0 to A23
| - | Monitoring / Control System | bar: A0 to A23
Rotating machines
| J52 | Motor, LV | A0: 1; A8: 1; A12: 1; A18: 1; A22: 3; A23: A | 21, 32
| J53 | Generator, LV | bar: A0 to A23
Related Job aids and Work Execution standards are guidelines only and not part of the policy and procdure
Comments
| 1 | For hermetically sealed oil-filled transformers without N2 blanket an oil sample analysis is not requested unless deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets)
| 2 | Sealed Minimum Oil Breakers are not included.
| 3 | Test is not required for double insulated devices
| 4 | Only applicable for external/outside buses and only if deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets)
| 5 | Recommendation for schedule is derived from NETA and IEEE: 25% of life expectancy or 2 years - whatever is less
| 6 | Only required if deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets); usually not done for single motor cables
| 7 | Tests are not required if the battery system is continuously monitored with a battery management system, providing similar functionality as described in the Job Aid J15
| 8 | Tests are required only for battery systems that supply plant critical loads (eg for HV protection relays, emergency systems or UPS systems)
| 9 | Only required for sockets which are not protected by GFCI/RCD
| 10 | Only required if no calculation document or specific MOC-procedure is in place
| 11 | 25% of the installed devices (randomly selected) within each plant area shall be tested. A 100% follow-up testing is required if the failure rate exceeds 2%.
| 12 | A sampling tests is sufficient. Select test points in all plant areas.
| 13 | Test is only required if it cannot be ensured that the portable tool is always used with a portable GFCI/RCD
| 14 | It is required that all portable tools and extension cords in the field are used with portable GFCI/RCD. In cases where - due to whatever reason - an upstream GFCI/RCD is not used, only tools and devices shall be used which are regularly tested (quarterly) as indicated by the EMP.
| 15 | Monthly test to verify lights go on and a yearly capacity test for all lamps for the time as specified by local code.
| 16 | Monthly functional tests are not required for emergency lighting systems that are monitored continously - a visual check of the indicaiton is sufficient
| 17 | Frequency for classified (ATEX Class 1/2 Div 1/2) areas is reduced to once per year
| 18 | Mandatory for overcurrent protection functions (ANSI/IEEE 50/51) and for earth fault protection functions (ANSI/IEEE 50N/51N); Recommended for all other protection functions
| 19 | Circuit breakers should be fully inspected after a severe high energy shutdowns (eg if trip was caused by short time or instantaneous or magnetic trip or if there is proof of a short circuit or arc downstream which was cleared by the breaker)
| 20 | Only applicable if fitted (usually ACB, PCB and ICCB do not have fuses inside, but some will have it, especially in NA)
| 21 | Due to the amount of LV motors installed and operated at Cargill facilities it is recommended to limit the scope to the following LV motors: Only black and grey assets which are • Difficult to replace (eg big motors, motor in difficult locations, etc.) OR • Expensive (eg big motors, classified areas, special motors etc.) OR • No spare parts available OR • Do cause a significant downtime or production cost which exceeds the maintenance costs over the lifetime of the motor The selection of the motors subject to receive maintenance is made by the local RE team
| 22 | An additiional preventive replacement program is suggested on top of the inspections in the matrix - refer to job aid for further information
| 23 | Not used
| 24 | PD measurement for 6kV and above only as part of the surge testing
| 25 | PD recommended as additional fault finding tool if tan delta or insualtion resistances measurement indicates issues; Offline PD in combination with VLF is preferred.
| 26 | Infrared testing for cable connections is included in the equipment connected to the cable and is not listed for the cable iself. Infrared of cables on raceways is not foreseen.
| 27 | Tests A08, A09 and A14 only need to be executed if they are not already executed together with the testing of the motor (motors can be tested from the MCC drawer/bucket, which will also test the components in between)
| 28 | Test A08 shall only be required if the heat trace circuit is not protected with a GFCI/GFEP/RCD
| 29 | It is recommended to test HT systems yearly before the start of the cold season to ensure they are operational
| 30 | The individual job aids do not distinguish between Safety and RE specific inspeciton points. While only the safety relevant points are required to be checked during the visual inspection it is recommended to include all RE ones as the addional required to execute the task is usually estimated to be minimal
| 31 | Test is not required, if the facility has all socket outlets protected with fixed mounted RCD/GFCI
| 32 | Online MCA not a mandatory test - see position paper E-PP-003 Online MCA for further guidance. It is only allowed to execute Online MCA if it can be done safely, as described in the position paper E-PP-003.
| 33 | Sampling inspection for detaield and close inspeciton possible for high quantity items of same equipment in the same environment - see WE standard A22 for details
| 34 | This inspection is required by IEC code for countries regulated by IEC and by ATEX for the European Union
| 35 | Adjust the schedule on the overall conditions and the ambient conditions. A suspicion or finding during the visual inspection A0 can warrant an immedeate physical inspeciton out of the normal scheduled inspection.
v
v
v
v
v
v
v
v
v
v
v
v
v
Note on D1: Comment 30: The individual job aids do not distinguish between Safety and RE specific inspeciton points. While only the safety relevant points are required to be checked during the visual inspection it is recommended to include all RE ones as the addional required to execute the task is usually estimated to be minimal
Note on AA1: Andreas Lehr: Do we want to write a WE standard for online MCA as well: It is currently mentiuoend in the job aids
Note on Z2: Comment 34: This inspection is required by IEC code for countries regulated by IEC and by ATEX for the European Union
Note on F4: Comment 1: For hermetically sealed oil-filled transformers without N2 blanket an oil sample analysis is not requested unless deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets)
Note on F5: Comment 1: For hermetically sealed oil-filled transformers without N2 blanket an oil sample analysis is not requested unless deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets)
Note on R9: Comment 19: Circuit breakers should be fully inspected after a severe high energy shutdowns (eg if trip was caused by short time or instantaneous or magnetic trip or if there is proof of a short circuit or arc downstream which was cleared by the breaker)
Note on R10: Comment 19: Circuit breakers should be fully inspected after a severe high energy shutdowns (eg if trip was caused by short time or instantaneous or magnetic trip or if there is proof of a short circuit or arc downstream which was cleared by the breaker)
Note on F11: Comment 2 This test applies only for Bulk Oil Circuit Breakers, but not for Minimum Oil Circuit Breakers (see Job Aid J16 for details)
Note on R11: Comment 19: Circuit breakers should be fully inspected after a severe high energy shutdowns (eg if trip was caused by short time or instantaneous or magnetic trip or if there is proof of a short circuit or arc downstream which was cleared by the breaker)
Note on R12: Comment 19: Circuit breakers should be fully inspected after a severe high energy shutdowns (eg if trip was caused by short time or instantaneous or magnetic trip or if there is proof of a short circuit or arc downstream which was cleared by the breaker)
Note on C19: Comment 4: Only applicable for external/outside buses and open switchgear/switchboards and only if deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets)
Note on R20: Comment 18: Mandatory for overcurrent protection functions (ANSI/IEEE 50/51) and for earth fault protection functions (ANSI/IEEE 50N/51N); Recommended for all other protection functions
Note on E25: Comments 6 Only required if deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets)
Note on G25: Comment 26r: IR for cable connections is included in the equipment connected to the cable and this not listed for the cable iself. IR of cables on raceways is not foreseen.
Note on I25: Comment 25: PD recommended as additional fault finding tool if tan delta or insualtion resistances measurement indicates issues; Offline PD in combination with VLF is preferred.
Note on L25: Comments 6 Only required if deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets)
Note on M25: Comments 6 Only required if deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets)
Note on O25: Comments 6 Only required if deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets)
Note on Y25: Comments 6 Only required if deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets)
Note on E26: Note 35: Adjust the schedule on the overall conditions and the ambient conditions. A suspicion or finding during the visual inspection A0 can warrant an immedeate physical inspeciton out of the normal scheduled inspection.
Note on I33: Comment 24: PD measurement for 6kV and above only as part of the surge testing
Note on I34: Comment 24: PD measurement for 6kV and above only as part of the surge testing
Note on N36: Comment 20: Only applicable if fitted (usually ACB, PCB and ICCB do not have fuses inside, but some will have it, especially in NA)
Note on R36: Comment 19: Circuit breakers should be fully inspected after a severe high energy shutdowns (eg if trip was caused by short time or instantaneous or magnetic trip or if there is proof of a short circuit or arc downstream which was cleared by the breaker)
Note on R37: Comment 19: Circuit breakers should be fully inspected after a severe high energy shutdowns (eg if trip was caused by short time or instantaneous or magnetic trip or if there is proof of a short circuit or arc downstream which was cleared by the breaker)
Note on N38: Comment 20: Only applicable if fitted (usually ACB, PCB and ICCB do not have fuses inside, but some will have it, especially in NA)
Note on R38: Comment 19: Circuit breakers should be fully inspected after a severe high energy shutdowns (eg if trip was caused by short time or instantaneous or magnetic trip or if there is proof of a short circuit or arc downstream which was cleared by the breaker)
Note on C42: Comment 4: Only applicable for external/outside buses and open switchgear/switchboards and only if deemed critical (major business impact or collateral damage) by Maintenance and Reliability (so called black assets)
Note on R45: Comment 5: Only required if deemed critical defined by maintenance and reliability definitions.
Note on R46: Comment 5 Only required if deemed critical defined by maintenance and reliability definitions.
Note on C47: Comment 22: An additiional preventive replacement program is suggested on top of the inspections in the matrix - refer to job aid for further information
Note on C48: Comment 22: An additiional preventive replacement program is suggested on top of the inspections in the matrix - refer to job aid for further information
Note on G50: Comment 26: IR for cable connections is included in the equipment connected to the cable and this not listed for the cable iself. IR of cables on raceways is not foreseen.
Note on E51: Note 35: Adjust the schedule on the overall conditions and the ambient conditions. A suspicion or finding during the visual inspection A0 can warrant an immedeate physical inspeciton out of the normal scheduled inspection.
Note on J54: Comment 7: Tests are not required if the battery system is continuously monitored with a battery management system, providing similar functionality as described in the Job Aid J15 Comment 8: Tests are required only for battery systems that supply plant critical loads (eg for HV protection relays, emergency systems or UPS systems)
Note on W54: Comment 5: Recommendation for schedule is derived from NETA and IEEE: 25% of life expectancy or 2 years - whatever is less Comment 8: Tests are required only for battery systems that supply plant critical loads (eg for HV protection relays, emergency systems or UPS systems)
Note on V58: Comment 17: Frequency for classified (ATEX, Class 1/2 Div 1/2) areas is reduced to once per year
Note on V62: Comment 9: Only required for sockets which are not protected by GFCI/RCD!
Note on X62: Comment 10: Only required if no calculation document or specific MOC-procedure is in place.
Note on R64: Comment 11: 25% of the installed devices (randomly selected) within each plant area shall be tested. A 100% follow-up testing is required if the failure rate exceeds 2%.
Note on V66: Comment 12: A sampling tests is sufficient. Select test points in all plant areas.
Note on L70: Comment 28: Test A08 shall only be required if the heat trace circuit is not protected with a GFCI/GFEP/RCD
Note on W70: Comment 29: It is recommended to execute this test before the winter periode to ensure the system is operable
Note on L72: Andreas Lehr: Removed all electrical tests (A08, A14, A18) because it is not an OEM requirement. From a risk profile the damage of the short pigtail which usually is hanging on the socket is reduced compared to the long extension cords that are laying on the ground.
Note on R72: Andreas Lehr: Removed all electrical tests (A08, A14, A18) because it is not an OEM requirement. From a risk profile the damage of the short pigtail which usually is hanging on the socket is reduced compared to the long extension cords that are laying on the ground.
Note on V72: Andreas Lehr: Removed all electrical tests (A08, A14, A18) because it is not an OEM requirement. From a risk profile the damage of the short pigtail which usually is hanging on the socket is reduced compared to the long extension cords that are laying on the ground.
Note on C73: Comment 14: It is required that all portable tools and extension cords in the field are used with portable GFCI/RCD. In cases where - due to whatever reason - an upstream GFCI/RCD is not used, only tools and devices shall be used which are regularly tested (quarterly) as indicated by the EMP.
Note on E73: Comment 13: Test is only required if it cannot be ensured that the portable tool is always used with a portable GFCI/RCD
Note on L73: Comment 13: Test is only required if it cannot be ensured that the portable tool is always used with a portable GFCI/RCD
Note on V73: Comment 3: Test is not required for double insulated devices Comment 13: Test is only required if it cannot be ensured that the portable tool is always used with a portable GFCI/RCD
Note on L74: Comment 31: Test is not required, if the facility has all socket outlets protected with fixed mounted RCD/GFCI
Note on V74: Comment 3: Test is not required for double insulated devices Comment 31: Test is not required, if the facility has all socket outlets protected with fixed mounted RCD/GFCI
Note on W79: Comment 15: Monthly test to verify lights go on and a yearly capacity test for all lamps for the time as specified by local code. Comment 16: Monthly functional tests are not required for emergency lighting systems that are monitored continously - a visual check of the indicaiton is sufficient
Note on C84: Comment 21: Due to the amount of LV motors installed and operated at Cargill facilities it is recommended to limit the scope to the following LV motors: Only black and grey assets which are • Difficult to replace (eg big motors, motor in difficult locations, etc.) OR • Expensive (eg big motors, classified areas, special motors etc.) OR • No spare parts available OR • Do cause a significant downtime or production cost which exceeds the maintenance costs over the lifetime of the motor The selection of the motors subject to receive maintenance is made by the local RE team.
Note on M84: Andreas Lehr: Discussion with CCC EMEA - they see need to check terminations. This is in line with NETA MTS 2015, but would require to open the temrinal box - and for US to remove the electric tape …... Do we want to add contact resistance or re-torquing as part of A1? COE Meeting 03.10.2019 - risk of introducing a new failure mode is bigger than the benefit we expect to get. LEave it out
Note on W85: Andreas Lehr: according to NFPA 110 Should be for critical loads RE

## Change Notes
Version | Date | Author | Changes
1.9 | - | AL | Added comment 26
| - | AL | Added test A19 for LV and HV switchboards
| - | AL | Deleted A17 for LV motors and LV generators in line with job aids
| - | AL | Added comment 19 for all breakers (requirement for testing after trip)
| 20.05.18 | AL | Changed test cycle for electrical test og J3 from 5 to 1 year (COE conference call)
| 20.05.18 | AL | Added notes 21 and 27 to J35 (FWS) to exclude electrical tests if the LWS is included in the test circuit from the MCC for the motor and + limit scope
| 20.05.18 | AL | Changed load test frequency A19 from 1 to 2 years for batteries J15 (COE conf call)
1.9A | 25.05.18 | AL | Added job aid numbers J44 - 48 and J12
| 25.05.18 | AL | Make all tests A18 as safety relevant
| 25.05.18 | AL | Clarity on Ground resistance versus Ground continuity - remove all A17 except for J31 as we only check the continuty to gorund, but not gorund itself
| 25.05.18 | AL | Added A18 for J47 and J48
1.9B | 19.11.18 | AL | Added note 30 for visual inspection A0
| 19.11.18 | AL | Added general note that job aids and work execution standards are guideline only
| 19.11.18 | AL | Removed electrival testing requirements for portable GFCI/RCD (J03)
2 | 19.11.18 | AL | Approved version 1.9B after COE conference call
2.0A | 28.05.19 | AL | Deleted PM and PdM in header row as they do not match to the definitions used in RE
Changed J17/A15 from 1-2 to 3-5 to be in line with the LV switch test schedule
Added J45/A1 and J45/A18 in line with job aids - in line with LV bus bar
Deleteted J45/A11 since it is not pratical
Added J43/A4 and J43/A11 in line with job aid
Added J44/A19 - in line with LV PFC units
Added J40/A7 - in line with HV bus ducts (only for fault finding and comissioning)
Added J42/A19 - in ine with job aid (called the functional test of the PFC unit out as A19 in the job aid)
2.1 |  |  | Approved version 2.0A after COE conference call
2.1 A | 18.12.19 | AL | Changed schedule for A3 (IR) and A4 (UE) from 1 to 1-3 years and made it mandatory (alignment with Insurance)
| 18.12.19 | AL | Made oil sampling for transformers J4A2 and J5A2 mandatory (alignment with Insurance), added comment 38
| 18.12.19 | AL | Added instrumentation as new line
| 18.12.19 | AL | Added notes 33 and 34 for IEC Ex inspections
| 18.12.19 | AL | Changed J2A22 to yearly and added comment 40
| 18.12.19 | AL | Changed frequency of A22 from 3 to 2-3 and made it mandatory for EMEA (see comment 34)
| 20.01.20 | AL | Added notes 36-38 to explain which inspections A2, A3 and A4 are mandatory from the insurance point of view
| 27.01.20 | AL | Split A5 into Online and Offline PD (A24) and A11 into Power Factor and Tan Delta Testing (A25) - grouped the three VLF tests together
| 27.01.20 | AL | Added yearly recommended test J18A5, J45A5 and changed J60A5 from A to 1 (comment A26)
| 27.01.20 | AL | Added header Online and Offline testing and moved A1 to the section Offline Testing
| 02.03.20 | AL | Adopted comment 26 to fit also for UE and online PD and added it to HV cables A04 and A05
| 19.03.20 | AL | Moved online MCA (A23) to online seciton
| 19.03.20 | AL | Added offline MCA (A26) as new, additional test method for LV and HV motors
| 02.04.20 | AL | Added J31 as job aid reference for lightining protection - changes in J31 are pending
| 11.06.20 | AL | Changed A1 for proection relais form 1 yearly to 3-5 yearly to be in line with the secondary injection testing
| 11.06.20 | AL, BJ | Added A3 and A4 for HV overhead lines and LV overhead lines, as these are called out in the respective job aid J62
| 11.06.20 | AL | Deleted infrared testing for HV motors J50 - is not done for LV motors (would need to be deleted from J50)
| 11.06.20 | AL | Addedcomment 39 for loop impedenace A20
| 11.06.20 | AL | Added new equipment for Start/Stop stations and Emergency Stop circuits (yearly visual test) and TBP for A19/EM Switches + comment 41
| 2020-08-01 | AL | Simplified statement in comment 4
2.2 | 2020-08-27 | AL | Approved version 2.1A after COE conference call